## Summary
CDS | Ofgem DD:
Clearer inspection data is required for Complex Distribution Systems (CDS) sites to understand scope of works, specific site details, site asset health scores, risk scores, action threshold, site prioritisation, cost breakdown and planned intervention to justify inclusion in our draft determinations. CDS volumes have been reduced until this data is provided.
WWU Response: August 2025 CDS Intervention List
This is a population that will be further refined for accuracy as we progress through our survey schedule. The list of CDS sites provided is a list at a point in time when we are still completing a survey programme of our CDS sites. Should a higher risk asset be identified (following a survey or a gas leak) an updated risk priority list is created. 39 CDS Sites have been identified for intervention in RIIO-GD3 - the Details Tab provides the following information: Specific site details Risk scores following survey Site priority based on total site risk (some sites with a lower risk score have higher priority based on the risk assessment of the site specifics that are not currently included in our risk score calculation) Planned intervention type Cost breakdown

## Details_CDS
REF | CDS Name | Location | Postcode | Geographical Area | CDS Type | Risk Category | Programme Inclusion Driver | CDS Risk Score | No. Storeys | No. Risers | No. Laterals | No. Manifolds | Proposed Gas Pipeline Works | New AG pipework? | Existing Total AG Pipework | Total Estimated Cost | Reason for Intervention | Asset Corrosion Conditon (Heavy, Minimal, Minor) | Planned Intervention Measure (Replace, Refurb, Cut Off)
1 | Guildhall Shopping Centre | Exeter | EX4 3HP | South West | Shopping Centre | High | Risk Score | 5.6 | 5 | 2 | 3 | 4 | Install 100mm Mapress Riser - 2m. Install 100mm Mapress Riser - 7m. Install 100mm Mapress Lateral - 110m. Install 4 x 54mm Mapress Mainfolds. Install 2 x 63mm PE Single Servies. Install 7 x 63mm PE PIVs. Install 1 x 90mm PE MIV. | Yes | 131m |  | Heavy Corrosion on Manifold. Large Scale AG network with low gas usage. | Heavy. | Replace.
2 | Kingsway Shopping Centre | Newport | NP20 1EW | South Wales | Shopping Centre | High | Risk Score | 6.3 | 4 | 1 | 5 | N/A | Install 100mm Mapress Riser - 3m. Install 100mm Mapress Lateral - 36m. Install 100mm Mapress Lateral - 96m. Install 54mm Mapress Lateral - 72m. Install 1 x MIV. Install 2 x PIV. Install 63mm PE Single Service. Install 63mm PE Single Service - Terminating in Gas Kiosk. | Yes | 207m |  | Heavy Corrosion on Lateral Section of AG Pipework. Large Scale AG network with low gas usage. | Heavy. | Replace.
3 | Eagles Meadow Shopping Centre | Wrexham | LL13 8DG | North Wales | Shopping Centre | High | Risk Score | 5 | 4 | 2 | 1 | N/A | Install 125mm PE MIV. Install 3 x 6" ST AG LIVs. All associated refurbishment works for approx 200m of AG ST. | No | N/A |  | To install MIVs, PIVs and LIVs. | N/A | Refurb.
6 | Eastgate Shopping Centre | Gloucester | GL1 1XH | Central | Shopping Centre | High | Risk Score | 7.4 | 4 | 2 | 9 | 1 | Install 6m of 100mm Mapress Riser. Install 3m of 80mm Mapress Riser. Install 158m of 100mm Mapress Lateral. Install 9m of 80mm Mapress Lateral. Install 168m of 38mm Mapress Lateral Service Branches. Install 4 Point Mainfold - 42mm Mapress. Install MIV - 8" ST Main. | Yes | 347m |  | Heavy Corosion on Lateral Pipework. Poor installation of service branches. Damage to AG pipework. Heavy corrosion on Manifold. Low Gas Usage (2 Users) | Heavy. | Replace.
7 | Broadwalk Shopping Centre | Bristol | BS4 2QU | Central | Shopping Centre | High | Risk Score | 8.1 | 6 | N/A | N/A | N/A | Install 4 x 63mm PE Entries. Install 15m Mapress Lateral. Install 6m Mapress Riser. Install 2 x MIV. Install 5 x PIV. | Yes | 21m |  | 4" AG Pipework unknown conditon and route capped off on roof of shopping centre. | N/A | Replace.
8 | Teign School | Newton Abbot | TQ12 3JG | South West | School | Medium | Risk Score | 5 | 2 | N/A | N/A | N/A | 4" ST Service Refurbishment. Install 63mm PE Service terminating in Gas Kiosk. Install 63mm PE Service terminating in Surface Mounted Meterbox. Install 125mm PE MIV. Install 90mm PE MIV. Install 63mm PE MIV. | No | N/A |  | 2 x Single Services with heavy corrosion. 1 x Non compliant service. | Heavy. | Replace.
9 | South Dartmoor Community College | Ashburton | TQ13 7EW | South West | School | Medium | Risk Score | 6 | 3 | N/A | N/A | N/A | Install 7 x 63mm PE Single Services. Install 7 x 63mm PE PIVs. Install MIV. | N/A | N/A |  | Refurbishment works to be done and alterations to be made on single services. | Minimal. | Replace.
10 | Petroc College | Barnstaple | EX31 2BQ | South West | School | Medium | Valve Installations | 2.9 | 3 | N/A | N/A | N/A | Install Kisok x 2. Install 9 x 63mm PE PIVs. Install 3 x 125mm PE MIVs. | No | N/A |  | Refurbishment works to be done and alterations to be made on single services. | Minimal. | Refurb.
11 | Chosen Hill School | Gloucester | GL3 2PL | Central | School | Medium | Valve Installations | 2.2 | 3 | N/A | N/A | N/A | Install 2 x 63mm PE Single Services. Install 3 x 63mm PE PIVs. Install 75mm PE MIV. Install 2 x 90mm PE MIVs. | No | N/A |  | PIV chamber to be cleared for MP single service. | N/A | Refurb.
12 | Cleeve School & Sixth Form | Cheltenham | GL 52 8AE | Central | School | Medium | Valve Installations | 2.9 | 2 | N/A | N/A | N/A | Install 63mm PE Single Service within Gas Kiosk x 2. Install 6 x 63mm PE PIVs. Install 125mm PE MIV. Install 63mm PE MIV. Install 4" ST MIV. | No | N/A |  | PIV chambers to be cleared. | N/A | Refurb.
13 | Cheltenham General Hospital | Cheltenham | GL53 7AN | Central | Hospital | Medium | Risk Score | 3.2 | 3 | N/A | N/A | N/A | Install 3 x 63mm PE Single Services within Gas Kiosks. Install 4 x 180mm PE MIVs. | No | N/A |  | Valve installations | N/A | Refurb.
14 | Defence Academy Swindon | Swindon | SN6 8LA | Central | Military Base | Medium | Risk Score | 5.4 | 3 | N/A | N/A | N/A | Install 1 x 42mm Mapress Single Service. Install 1 x 54mm Mapress Single Service. Install 1 x 88mm Mapress Single Service. Install 3 x 63mm PE PIVs. | Yes | 12m |  | AG ST Single Services with heavy corrosion. | Heavy. | Replace.
15 | Exmouth Community College | Exmouth | EX8 3AF | South West | School | Medium | Risk Score | 4 | 3 | N/A | N/A | N/A | Install External Kiosk x 10. 63mm PE Service Alter x 6. Install 14 x 63mm PE PIVs. Install 90mm PE MIV x 4. | No | N/A |  | Single Services with Heavy Corrosion and Non Compliant Location. | Heavy. | Replace and Refrub.
16 | Beechen Cliff School | Bath | BA2 4RE | Central | School | Medium | Risk Score | 5.1 | 2 | N/A | N/A | N/A | 2 x 63mm PE Service Alterations. Install 180mm PE MIV. Install 63mm PE MIV. | N/A | N/A |  | Installation of MIV & PIV. Non Compliant Meter Positions. | N/A | Refurb.
17 | Cwmbran Shopping Centre | Cwmbran | NP44 1PB | South Wales | Shopping Centre | Medium | Degraded Paintwork and Corrosion on Manifolds | 2.9 | 3 | N/A | N/A | 2 | Install 2 x 50mm Mapress ST Manifolds. Install 6 x 63mm PE PIVs. Install 125mm PE MIV. | Yes | 12m |  | Refurb 5 x PIV. Install 1 x PIV. | N/A | Refurb.
18 | Barry Hospital | Barry | CF62 8YH | South Wales | Hospital | Medium | Valve Installations | 2.5 | 2 | N/A | N/A | N/A | Install 80mm Mapress ST Single Service. Install 63mm PE PIV. Install 90mm PE MIV. | Yes | 2m |  | Refurb PIV. | N/A | Refurb.
19 | Monmouth School for Girls | Monmouth | NP25 5XT | South Wales | School | Medium | Valve Installations | 1.6 | 3 | N/A | N/A | N/A | Install 80mm Mapress ST Single Service. Install 2 x 63mm PE Single Services. Install 3 x 63mm PE PIVs. Install 250mm PE MIV. | Yes | 2m |  | Refurb ST AG Entries. | Minimal. | Refurb.
21 | Fosse Way School | Radstock | BA3 3AL | Central | School | Medium | Valve Installations | 2.5 | 2 | N/A | N/A | N/A | Install 63mm PE Single Service within Gas Kiosk. Install 3 x 63mm PE PIVs. Install 2 x 63mm PE MIVs. | No | N/A |  | Install PIV & MIV. | N/A | Refurb.
22 | Ysbyty’r Tri Chwm | Ebbw Vale | NP23 6HA | South Wales | Hospital | Medium | Valve Installations | 2.9 | 1 | N/A | N/A | N/A | Install 80mm Mapress ST Single Service. Install 63mm PE PIV. Install 90mm PE MIV. | Yes | 2m |  | Install PIV & MIV. | N/A | Refurb.
23 | Ysbyty Cwm Cynon | Mountain Ash | CF45 4BZ | South Wales | Hospital | Medium | Valve Installations | 2.9 | 2 | N/A | N/A | N/A | Install 80mm Mapress ST Single Service. Install 63mm PE PIV. Install 90mm PE MIV. | Yes | 2m |  | Install PIV & MIV. | N/A | Refurb.
24 | Pontypridd Cottage Hospital | Pontypridd | CF37 4AL | South Wales | Hospital | Medium | Valve Installations | 2.5 | 3 | N/A | N/A | N/A | Install 2 x 80mm Mapress ST Single Service. Install 63mm PE PIV. Install 90mm PE MIV. | Yes | 2m |  | Install PIV & MIV. Install Supports on Single Service. | N/A | Refurb.
25 | Stroud High School | Stroud | GL5 4HF | Central | School | Medium | Risk Score | 3.2 | 2 | N/A | N/A | N/A | Install 63mm PE Single Service within Gas Kiosk. | No | N/A |  | MP Service Governors to be replaced. | Minimal. | Replace.
26 | Regent Arcade Shopping Centre | Cheltenham | GL50 1JZ | Central | Shopping Centre | Medium | Risk Score | 5.8 | 5 | N/A | N/A | N/A | Install 54mm Mapress AG Service. Install MIV - 4" Main. | Yes | 30m |  | PIV installation on 4" Service. | Minimal. | Replace.
28 | Exeter Retail Park | Exeter | EX2 8LH | South West | Shopping Centre | Medium | Risk Score | 3.2 | 2 | N/A | N/A | N/A | Install 4 x 63mm PE Single Service within Gas Kiosk. Install 90mm PE MIV. |  |  |  | Alteration of a NON compliant service. Refurb work on single services. | N/A | Refurb.
29 | Torbay Hospital | Torquay | TQ2 7AA | South West | Hospital | Medium | Risk Score | 4.9 | 5 | N/A | N/A | 4 | Install 12 x 63mm PE PIVs. Install 4 x 54mm Mapress ST Manifolds - 10m. Install 2 x MIV - 18" SI. Install 2 x MIV - 125mm PE. | Yes | 12m |  | 12 x PIV Installation. Refurbishment works to be done on corroded manifolds. MIV to be installed. | Minimal. | Refurb.
30 | St Bonnifaces College | Plymouth | PL5 3AG | South West | School | Medium | Risk Score | 5.1 | 3 | N/A | N/A | N/A | Install 125mm PE MIV. Decommission 2" ST Service. | No | N/A |  | PIV & MIV installation. Decommission of single service. | N/A | Refurb.
31 | Mount Gould Hospital | Plymouth | PL4 7QD | South West | Hospital | Medium | Risk Score | 3.8 | 4 | N/A | N/A | N/A | Install 100mm ST Single Service. Install 4 x 125 PE MIVs. | Yes | 5m |  | Large Scale replacement works to be done on single service. | Heavy. | Replace.
60 | Southway Centre Plymouth | Plymouth | PL6 6QR | South West | Shopping Centre | Medium | Interim Repair | 2.1 | 2 | 1 | 1 | N/A | Install 50mm Mapress ST Riser - 3m. Install 50mm Mapress ST Lateral 110m. Install 63mm PE PIV. Install 90mm PE MIV. | Yes | 113m |  | Large Scale replacement of Riser & Lateral Pipework. | Minimal. | Replace.
269 | The Brunel Shopping Centre | Swindon | SN1 1LF | Central | Shopping Centre | High | Risk Score | 5.8 | 4 | 3 | 3 | 3 | All associated refurbishment works (sanding and repainting) for approx 670m of AG ST. Install 125mm PE MIV. | Yes | 670m |  | Large Scale Internal AG Network - Low Gas Users and Overbuild. | Minimal. | Refurb.
276 | Drake Circus | Plymouth | PL1 1EA | South West | Shopping Centre | Medium | Risk Score | 4.9 | 9 | 3 | 3 | 4 | Refurbishment Works to be done on approx 150m of AG ST pipework. Install 250mm PE MIV. Install 180mm PE MIV. Install 180mm PE PIV. Install 125mm PE PIV. | Yes | 150m |  | MIV & PIVs to be fitted. Refurbishment work to be done on pipework. | Minimal. | Refurb.
300 | Cribbs Causeway Retail Park | Bristol | BS34 5DG | Central | Shopping Centre | High | Risk Score | 4.3 | 4 | 4 | 4 | N/A | Install 6 x 76mm Mapress ST Risers - 6m. Install 1480m of Lateral AG 54mm Mapress ST. Install 6 x 63mm PE PIVs. Install 250 PE MIV | Yes | 1516m |  | Replacement of all AG pipework. | Heavy. | Replace.
372 | RAF Brize Norton | Carterton | OX18 3LX | Central | Military Base | Medium | Risk Score | 5 | 3 | N/A | N/A | N/A | Refurbishment works to be done on MP Governors. |  | 40m (Small MP Governors) |  | Refurbishment works to be done on MP Governors. | Minimal. | Refurb.
390 | St Margaret's Prep School | Calne | SN11 0DF | Central | School | Medium | Risk Score | 3.75 | 2 | N/A | N/A | N/A | Install 63mm PE Single Service within Gas Kiosk. | No | N/A |  | Replace Single Service Meterboxes. | Minimal. | Refurb.
75 A | St Lawrence House | Bath | BA1 1TP | Central | Shopping Centre | Medium | Risk Score | 4.3 | 3 | 1 | 1 | 1 | Refrubishment works of 35m of 50mm ST. Install 63mm PE PIV. Install 250mm PE MIV. | No | N/A |  | Future Refurb & Maintainance to AG Pipework. Installation of MIV. | Minor. | Refurb.
75 B | Southgate House | Bath | BA1 1TP | Central | Shopping Centre | Medium | Risk Score | 4.3 | 4 | 1 | 2 | 2 | Install 80mm ST Riser. Refrubishment works on 150m of 50mm ST. Install 90mm PE PIV. Install 2 x 180mm PE MIVs. | Yes | 6m |  | Refrubishment works on AG Pipework. Installation of MIV. | Minimal. | Refurb.
75 C | Marchant House | Bath | BA1 1TP | Central | Shopping Centre | Medium | Risk Score | 4.3 | 5 | 1 | 1 | N/A | Install 76mm Mapress ST Riser. Install 90mm PE PIV. Install 2 x 180mm PE MIV. Refurbishment works of 100m of 50mm ST. | Yes | 6m |  | Alteration of a NON compliant service. Futrue Refurb Work & Maintainance. Installation of MIV. | Minor. | Refurb.
75 D | Phillip House | Bath | BA1 1TP | Central | Shopping Centre | Medium | Risk Score | 4.3 | 5 | 1 | 3 | 2 | Install 76mm Mapress ST Riser. Install Aprox 20m of 50mm AG Mapress ST. Install 90mm PE PIV. Install 90mm PE MIV. | Yes | 26m |  | Future Refurb & Maintainance to AG Pipework. Installation of MIV. | Minor. | Refurb.
75 E | Southgate Place | Bath | BA1 1TP | Central | Shopping Centre | Medium | Risk Score | 4.3 | 5 | N/A | N/A | 1 | Install 76mm Mapress ST 5 Point Manifold. Install 90mm PE MIV. | Yes | 10m |  | Future Refrub & Maintainance to AG Pipework. Installation of MIV. | Minor. | Refurb.
75 F | Dorchester House | Bath | BA1 1TP | Central | Shopping Centre | Medium | Risk Score | 4.3 | 4 | N/A | N/A | 1 | Install 76mm Mapress ST 6 Point Manifold. Install 90mm PE MIV. | Yes | 12m |  | Future Refrub & Maintainance to AG Pipework. Installation of MIV. | Minor. | Refurb.