## GD3 Price Breakdown
Submission | Asset Type | Intervention Driver | Asset Data |  |  |  | Avg replacement per Price control |  | RIIO:GD3 Submission |  |  | Variance |  | Faults |  | No. Intervention Rating Rag |  |  |  | Intervention Rating Rag % |  |  |  | Strategy
|  |  | Asset Numbers | Average Age | Lifecycle | Price Control Duration | % per control | Volume per control | Volume Requested | Cost of Intervention | % per Control | Volume Diff | % Diff | ESS Fault Raised |  | R | A | R&A | G | R | A | R&A | G
LT AGI E&I | MAINS AND SUB MAINS DISTIBUTION | Condition | 307 | 2013 | 25 | 5 | 20% | 61.4 | 23 |  | 7.492% | -38.4 | -12.51% | 493 |  | 0 | 30 | 30 | 277 | 0% | 9.772% | 9.772% | 90.23%
LT AGI E&I | LIGHTING | Condition | 307 | 2013 | 20 | 5 | 25% | 76.75 | 42 |  | 13.68% | -34.75 | -11.32% | 158 |  | 0 | 76 | 76 | 231 | 0% | 24.76% | 24.76% | 75.24%
LT AGI E&I | MAINS INTAKE | Condition | 307 | 2013 | 25 | 5 | 20% | 61.4 | 24 |  | 7.818% | -37.4 | -12.18% | 69 |  | 0 | 31 | 31 | 276 | 0% | 10.1% | 10.1% | 89.9%
LT AGI E&I | SECURITY CCTV INSTALLATION | Condition | 20 | 2013 | 15 | 5 | 33.33% | 6.6667 | 5 |  | 25% | -1.6667 | -8.333% | 5 |  | 0 | 18 | 18 | 2 | 0% | 90% | 90% | 10%
LT AGI E&I | PRE_HEAT ELECTRICAL HEATERS | Condition | 29 | 2012 | 20 | 5 | 25% | 7.25 | 0 |  | 0% | -7.25 | -25% | 13 | 13 | 0 | 26 | 26 | 3 | 0% | 89.66% | 89.66% | 10.34%
LT AGI E&I | GENERATOR STANDBY POWER SYSTEM | Condition | 35 | 2014 | 15 | 5 | 33.33% | 11.6667 | 3 |  | 8.571% | -8.6667 | -24.76% | 40 |  | 3 | 0 | 3 | 32 | 8.571% | 0% | 8.571% | 91.43%
LT AGI E&I | PSUP MAINS DISTRIBUTION | Condition | 6 | 2017 | 20 | 5 | 25% | 1.5 | 0 |  | 0% | -1.5 | -25% | 0 | 0 | 0 | 0 | 0 | 6 | 0% | 0% | 0% | 100%
LT AGI E&I | LGT SYSTEM | Condition | 17 | 2014 | 20 | 5 | 25% | 4.25 | 5 |  | 29.41% | 0.75 | 4.412% | 391 |  | 5 | 0 | 5 | 12 | 29.41% | 0% | 29.41% | 70.59%
LT AGI E&I | GAS CHROMOTOGRAPHY | Condition | 16 | 2019 | 20 | 5 | 25% | 4 | 1 |  | 6.25% | -3 | -18.75% | 79 |  | 0 | 1 | 1 | 15 | 0% | 6.25% | 6.25% | 93.75%
LT AGI E&I | FIELD INSTRUMENT | Condition | 307 | 2016 | 15 | 5 | 33.33% | 102.3333 | 52 |  | 16.94% | -50.3333 | -16.4% | 694 |  | 9 | 57 | 66 | 241 | 2.932% | 18.57% | 21.5% | 78.5%
LT AGI E&I | PSUP ADACS & ALARM SYSTEM | Condition | 6 | 2017 | 15 | 5 | 33.33% | 2 | 0 |  | 0% | -2 | -33.33% | 0 | 0 | 6 | 0 | 6 | 0 | 100% | 0% | 100% | 0%
LT AGI E&I | TELEMETRY & BARRIER SYSTEM | Obsolencence | 307 | 2014 | 15 | 5 | 33.33% | 102.3333 | 52 |  | 16.94% | -50.3333 | -16.4% | 72 |  | 25 | 190 | 215 | 92 | 8.143% | 61.89% | 70.03% | 29.97%
LT AGI E&I | E/P CONTROLLER | Obsolencence | 20 | 2005 | 15 | 5 | 33.33% | 6.6667 | 20 |  | 100% | 13.3333 | 66.67% | 16 |  | 20 | 0 | 20 | 0 | 100% | 0% | 100% | 0%
LT AGI E&I | FLOW COMPUTER | Obsolencence | 17 | 2005 | 15 | 5 | 33.33% | 5.6667 | 8 |  | 47.06% | 2.3333 | 13.73% | 18 |  | 2 | 14 | 16 | 1 | 11.76% | 82.35% | 94.12% | 5.882%
LT AGI E&I | IND COMPUTER | Obsolencence | 16 | 2005 | 15 | 5 | 33.33% | 5.3333 | 7 |  | 43.75% | 1.6667 | 10.42% | 0 |  | 5 | 9 | 14 | 2 | 31.25% | 56.25% | 87.5% | 12.5%
LT AGI E&I | UPS SYSTEMS (LARGE) | Obsolencence | 24 | 2014 | 15 | 5 | 33.33% | 8 | 5 |  | 20.83% | -3 | -12.5% | 74 |  | 3 | 5 | 8 | 16 | 12.5% | 20.83% | 33.33% | 66.67%
LT AGI E&I | FISCAL METERING | Condition | 17 | 2012 | 15 | 5 | 33.33% | 5.6667 | 5 |  | 29.41% | -0.66667 | -3.922% | 26 |  | 4 | 1 | 5 | 12 | 23.53% | 5.882% | 29.41% | 70.59%
LT AGI E&I | Type 2 SPD Installations | Safety & Compliance | 307 | N/A | 25 | 5 | 20% | 61.4 | 50 |  | 100% | -11.4 | 80% | No Current Fault Data / Not fault driven | [9 empty] | Fit SPD's to sites with highest strike rate/km2
LT AGI E&I | Replace Gas Chromatograph Secondary Instrumentation | Condition | 16 | 2019 | 15 | 5 | 33.33% | 5.3333 | 5 |  | 31.25% | -0.33333 | -2.083% | 5 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LT AGI E&I | SCOFF Sites to SCADA | Supply Resiliance | 0 | N/A | 15 | 5 | 0% | 0 | 15 |  | 100% | 15 | 100% | No Current Fault Data / Not fault driven | [9 empty] | Telemeter 15 Key sites back to SCADA
LT AGI E&I | UPS System Battery Replacements | Condition | 60 | N/A | 5 | 5 | 100% | 60 | 60 |  | 100% | 0 | 0% | 783 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LT AGI E&I | Telemetry HMI Replacements | Condition | 307 | N/A | 15 | 5 | 33.33% | 102.3333 | 20 |  | 6.515% | -82.3333 | -26.82% | 8 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LT AGI E&I | GPRS Replacement (2G/3G Comms) | Obsolecence | 307 | 2012 | 15 | 5 | 33.33% | 102.3333 | 180 |  | 58.63% | 77.6667 | 25.3% | 46 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Replace 85% of units in GD3 at highest risk sites
LT AGI E&I | Satellite Routers Replacement | Obsolecence | 307 | 2012 | 15 | 5 | 33.33% | 102.3333 | 100 |  | 100% | -2.3333 | 66.67% | Logged via OEM |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Replace 50% of units in GD3, to create spares
LT AGI E&I | Net 0 - Smart Systems | Biomethane Entry | 0 | N/A | 15 | 5 | 0% | 0 | 19 |  | 100% | 19 | 100% | No Current Fault Data / Not fault driven | [9 empty] | Adapt control philosophy on three networks
LT AGI E&I | Field Asset Equipment Failures | Condition | 10 | N/A | 5 | 5 | 100% | 10 | 10 |  | 100% | 0 | 0% | 67 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LT AGI E&I | Heat Exchanger Burst Disc Replacements | Condition | 60 | N/A | 5 | 5 | 100% | 60 | 60 |  | 100% | 0 | 0% | 23 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LT AGI E&I | Solar Panel Installations | Environmental | 0 | N/A | 25 | 5 | 0% | 0 | 5 |  | 100% | 5 | 100% | No Current Fault Data / Not fault driven | [9 empty] | Undertake 5 projects across the network
LT AGI E&I | P4T & P6T Instrument Impulse Valve replacements | Safety & Compliance | 27 | N/A | 15 | 5 | 0% | 0 | 18 |  | 66.67% | 18 | 66.67% | No Current Fault Data / Not fault driven | [9 empty] | Replace valves in GD3 to remove the risk
LT AGI E&I | Sixnet Telemetry RTU Replacements | Obsolecence | 215 | 2012 | 15 | 5 | 33.33% | 71.6667 | 160 |  | 74.42% | 88.3333 | 41.09% |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Replace circa 40% of units in GD3 to create spares
TOTAL | [8 empty] | 954 | [14 empty] | Strategy
<7Bar PM | DG ELECTRICAL REBUILD | Condition | 36 | 2012 | 25 | 5 | 20% | 7.2 | 5 |  | 13.89% | -2.2 | -6.111% | 35 |  | 0 | 5 | 5 | 31 | 0% | 13.89% | 13.89% | 86.11%
<7Bar PM | PRESSURE MANAGEMENT EQUIPMENT | Condition | 3987 | Various | 15 | 5 | 33.33% | 1329 | 1580 |  | 39.63% | 251 | 6.295% | 1039 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
<7Bar PM | VALIDATION LOGGERS | Condition | 548 | Various | 15 | 5 | 33.33% | 182.6667 | 180 |  | 32.85% | -2.6667 | -0.4866% | 128 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TOTAL | [8 empty] | 1765
| LTS AGI Intervention Driver | Average Vol per control | GD3 Vol | % Vol | GD3 Cost | % Cost
| Obsolencence | 404.3333 | 532 | 55.77% | 0 | #DIV/0! | [5 empty] | R | Intervention Required
| Condition | 582.55 | 315 | 33.02% | 0 | #DIV/0! | [5 empty] | A | Plan
| Biomethane Entry | 0 | 19 | 1.992% | 0 | #DIV/0! | [5 empty] | G | Monitor
| Environmental | 0 | 5 | 0.5241% | 0 | #DIV/0!
| Supply Resiliance | 0 | 15 | 1.572% | 0 | #DIV/0!
| Safety & Compliance | 61.4 | 68 | 7.128% | 0 | #DIV/0!
|  | 1048.2833 | 954 | 100% | 0 | #DIV/0!
| LTS AGI Intervention Driver | Average Vol per control | GD3 Vol | % Vol | GD3 Cost | % Cost
| Condition | 1518.8667 | 1765 | 100% | 0 | #DIV/0!
|  | 1518.8667 | 1765 | 100% | 0 | #DIV/0!