| # Briefing Note 11: Completion Files |  |
| --- | --- |
| Version 1.0 January 2023 |  |

Table of Contents

1)	Introduction	3

2)	Utility Infrastructure Provider (UIP) Criteria	4

2.1) UIP New Lay/Alteration/Disconnection 63mm and below (LP/MP)	4

2.2) UIP New Lay/Alteration/Disconnection other	5

2.3) Partial Completion Files	6

3)	Independent Gas Transporter (IGT) Connected System Exit Point (CSEP) Criteria	7

3.1) CSEP 63mm and below (LP/MP)	7

3.2)	CSEP other	8

4)	Pneumatic and Hydrostatic Pressure Testing	9

5)	As-Laid Drawing	10

6)	Photographic Evidence	11

7)	Mains Location Arrangements	12

8)	Appendices	12

Appendix A – New Service As-Laid Plan	12

Appendix B – New Main and Service As-Laid Plan	13

Appendix C – Alteration As-Laid	13

Appendix D – Disconnection As-Laid	14

Appendix E – CSEP As-Laid Plan	14

Appendix F – DR8 Plan	15

Appendix G – Unsuitable As-Laid	15

Introduction

Completion Files must be sent to Wales & West Utilities (WWU) Third Party Connections within D+10 of the date of Substantial Completion, as defined in WWU Final Connections Agreement (FCA), Section 1 Interpretation. WWU will liaise with third parties automatically via email for outstanding completion files where the Substantial Completion date has passed.

Completion File minimum information requirements are outlined within this Briefing Note and are based on criteria outlined in IGEM Specification TD/101.

WWU will appraise the contents of a Completion file and where minimum information is not met, will reject the Completion file via email.

WWU hold the right to refuse any further new requests from third parties who fail to provide Completion Files within the agreed timescales or where requested by WWU.

The criteria outlined in this briefing note is an absolute minimum, but any additional documentation or supporting information that is obtained on site should be supplied as part of the completion file to WWU.

Please note – All standards of service start on the date of connection/disconnection, not the date that all onsite works are complete.

Utility Infrastructure Provider (UIP) Criteria

Different UIP work steams facilitated by Third Party Connections have different minimum information requirements, as listed below.

- 2.1) UIP New Lay/Alteration/Disconnection 63mm and below (LP/MP)

Scaled As-Laid, including:

  - Full extent of works

  - Depth of cover of any remaining pipe or new lay at appropriate intervals (including connection/disconnection point)

  - Scaled dimensions from permanent fixtures

  - Date of connection/alteration/disconnection

  - Name of UIP company

  - Name of individual who produced As-Laid

  - Connection/Disconnection point Eastings and Northings

  - Scale (to Industry standard)

  - Description of works

  - Relevant WWU and third party references

WWU Completion File Cover Page, including:

  - Relevant WWU and third party references

  - Site Address

  - Additional Information

Pressure Test/FM144/FM166

MPRN(s)

  - If an existing MPRN is to be retained, this must be identified. If the existing MPRN is not to be retained and a new MPRN has been raised, list both new and existing MPRNs and state which MPRN is to be set to Dead on Xoserve UK Link

Valve record card including serial numbers, for all valves

Asset Error report (DR8), if applicable

FM183 Variation Form, if applicable

- 2.2) UIP New Lay/Alteration/Disconnection other

- Scaled As-Laid, including:

  - Full extent of works

  - Depth of cover of any remaining pipe or new lay at appropriate intervals (including connection/disconnection point)

  - Scaled dimensions from permanent fixtures

  - Date of connection/alteration/disconnection

  - Name of UIP company

  - Name of individual who produced As-Laid

  - Connection/Disconnection point Eastings and Northings

  - Scale (to Industry standard)

  - Description of works

  - Relevant WWU and third party references

- WWU Completion File Cover Page, including:

  - Relevant WWU and third party references

  - Site Address

  - Additional Information

- Routine or Non-Routine Operation record (RO/NRO under SCO) and clearance to proceed

- MPRN(s)

  - If an existing MPRN is to be retained, this must be identified. If the existing MPRN is not to be retained and a new MPRN has been raised, list both new and existing MPRNs and state which MPRN is to be set to Dead on Xoserve UK Link

- Valve record card including serial numbers, for all valves

- Asset Error report (DR8), if applicable

- FM183 Variation Form, if applicable

- Separate Pressure test for Under Pressure Tees (UPT) and Branch Saddle connections

- 2.3) Partial Completion Files

Where a project is going to take longer to complete than 5 working days (from the date of connection), the UIP required to submit a Partial Completion File.

A Partial Completion File should contain all of the relevant documentation stated above for the work carried out up to that point.

For projects that will take longer than 10 working days to complete, a Partial Completion File is required every 5 working days, until the project is complete.

Every submission must include a “UIP Completion File Cover” Form, please specify that it is a Partial Completion File and in the summary box, indicate how much work is outstanding.

Example:

Independent Gas Transporter (IGT) Connected System Exit Point (CSEP) Criteria

The multiple IGT work steams that Third Party Connections facilitate have different minimum information requirements, as listed below.

- 3.1) CSEP 63mm and below (LP/MP)

- Scaled As-Laid, including:

  - Depth of cover at connection point

  - At least two Scaled dimensions from permanent fixtures at connection point

  - Date of connection

  - Name of company undertaking works

  - Name of adopting IGT

  - Name of individual who produced As-Laid

  - Connection point Eastings and Northings

  - Scale (to Industry standard)

  - Description of works

  - Relevant WWU and third party references

- WWU Completion File Cover Page, including:

  - Relevant WWU and third party references

  - Site Address

  - Additional Information

- Pressure Test/FM144

- Construction Valve record card including serial number, if applicable

- Asset Error report (DR8), if applicable

- FM183 Variation Form, if applicable

  - CSEP other

- Scaled As-Laid, including:

  - Depth of cover at connection point

  - At least two Scaled dimensions from permanent fixtures at connection point

  - Date of connection

  - Name of company undertaking works

  - Name of adopting IGT

  - Name of individual who produced As-Laid

  - Connection point Eastings and Northings

  - Scale (to Industry standard)

  - Description of works

  - Relevant WWU and third party references

- WWU Completion File Cover Page, including:

  - Relevant WWU and third party references

  - Site Address

  - Additional Information

- Routine or Non-Routine Operation record (RO/NRO under SCO) and Clearance to Proceed

- Construction Valve record card including serial number, if applicable

- Asset Error report (DR8), if applicable

- FM183 Variation Form, if applicable

- Separate Pressure test for Under Pressure Tees (UPT) and Branch Saddle connections

Pneumatic and Hydrostatic Pressure Testing

Low pressure services should be pneumatically tested to 100mb for a period of no less than 5 minutes.

Low Pressure Mains should be pneumatically tested to 350mb, for a period as defined in IGEM Specification TD/3 Table 13.

Medium Pressure Services should be pneumatically tested to 3bar (1.5 x 2bar MOP) for a period of no less than 5 minutes.

Medium Pressure Mains should be pneumatically tested to 3bar (1.5 x 2bar MOP) for a period as defined in IGEM Specification TD/3 Table 13.

Intermediate Pressure Services should be pneumatically tested to 7bar for a period of no less than 5 minutes.

Intermediate Pressure Mains should be pneumatically tested to either 6 or 7bar, depending on the MOP for a period as defined in IGEM Specification TD/3 Table 13.

Where applicable, Hydrostatic Testing should be undertaking in addition to the above pneumatic requirements, as defined in IGEM Specification TD/3 Table 12. Where a new pipeline has been Hydrostatically tested, applicable drying certificates should be provided prior to commissioning.

As-Laid Drawing

It is essential that when dimensions are drawn onto the as-built drawing template that they refer to OS features, which will be shown on WWU’s graphical records system. Where shown, the following features should be used as reference points for dimensions:

- Buildings, Dimensions measured from buildings, should follow a line of sight from an element of the building structure.

- Kerb lines. Dimensioned pipe offsets from kerb lines should be placed at identifiable locations, e.g. where kerb lines are crossed by building sight lines, or boundary lines.

- Alternatively, the distance between dimensions should be recorded, provided at least one dimension is taken at a point where its position can be fixed in relation to OS map features.

- Boundary lines: Dimensions should be taken from other permanent features, such as boundary walls and boundary fence lines.

As examples, the following features should not be used as points of reference: Trees; Gullies; Street furniture.

It is necessary that all dimensions are specific and are easily identifiable in the field. Where connection positions are indicated, it is necessary to show at least two complementary dimensions so that the location may be found in the future.

If required, the third party may request a blank plan of the relevant area when submitting the plan date, in order to confirm the features that may be used for dimensions.

Please note – should the geography available on WWU’s plans be out of date and none of the features are shown, please contact Third Party Connections as soon as possible to discuss.

Photographic Evidence

As per the FCA, please be aware that WWU may request photographic evidence of the completed works.

Where the UIP is installing a manifold or a kiosk, photographic evidence must be provided with the completion file.

Should the customer wish to provide GPS co-ordinates on the as-laid drawing, a photograph/screen grab of the reading is required.

Mains Location Arrangements

A main location error is defined as an inaccuracy between WWU’s registered mapping database and what is identified on-site. The UIP/IGT is responsible for ensuring that the latest records are obtained from https://www.linesearchbeforeudig.co.uk/ and WWU will not accept any liability where other records are being used.

For further details, please see Briefing Note 13 – Mains Location Arrangements.

Appendices

Appendix A – New Service As-Laid Plan

Appendix B – New Main and Service As-Laid Plan

Appendix C – Alteration As-Laid

Appendix D – Disconnection As-Laid

Appendix E – CSEP As-Laid Plan

Appendix F – DR8 Plan

- Appendix G – Unsuitable As-Laid