| Briefing Note 5: # NP14 - The Design of System Extensions, Connections & Services to <7bar WWU Systems |  |
| --- | --- |
| Version 1.0 January 2023 |  |

Table of Contents

1)	Introduction	3

2)	Requirement for Network Analysis	3

3)	Appendix A Standard Design Tables	5

Table A.1.	5

Table A.2	6

Table A.3.	7

Table A.4	8

Table A.5	8

Table A.6	9

Table A.7	9

Table A.8	9

Table A.9	10

Table A.10	11

4)	Appendix B – Specification for the Design of Pipes	11

5)	Appendix C – Evaluation and Design of Connections to Non-Typical Demands	12

6)	Appendix D – Specification for Standard Pipe Code Table for New Lay Pipes	12

7)	Further Information	12

Introduction

The Design of System Extensions, Connections & Services to <7bar WWU Systems T/SP/NP/14/E (NP14) is Wales & West Utilities (WWU) Network Planning Specification Document used by Third Party Connections.

It sets out pressure parameters, pipe size minimums and restrictions for loads up to a certain threshold, which WWU set as an acceptable standard for use by third parties for design purposes.

In accordance with WWU’s Licence Condition 4B statement, standard source pressure tables for ‘guaranteed pressures’ have been included within NP14 to enable submissions using the “Fast Track Acceptance” process, where applicable.

Requirement for Network Analysis

All requests received for new or increased loads shall be assessed to determine if network analysis is required at the quotation stage. Refer to Appendix A Tables A.1. and A.2. If the request falls outside of the scope of Table A1 and Table A2, it shall be referred for network analysis.

Post Acceptance Security of Supply (SoS) assessment may be required when standard pressures have been taken from Tables A.2.

The SoS check shall be carried out to ensure that capacity is available to support the load increase. Any shortfall in capacity should be met, at Wales & West Utilities’ cost, before the load can be connected.

The process for undertaking post acceptance SoS checks and notifying the customer of any lead times for provision of capacity, shall be in accordance with connections and planning policies/procedures.

Please note: Reinforcement will not be planned for projects without planning permission.

All Non-Typical Gas Demands require assessment by Network Analysis and an Additional Load Information Form for Non-Typical Gas Demands is also required. See Briefing Note 5 – Non-Typical Gas Demands.

Projects that require Security of Supply checks or no Network Analysis may be submitted via the Fast Track process, loads that fall within Appendix A Tables A.1. and A.2.

Third Party Connections have designed a “Pressure Checker” Tool. By selecting the Job Type and Pressure Tier, and inputting the Parent Main Diameter, Parent Main Material and the required load(s) (in kWh), it will show if Network Analysis is required and the Guaranteed Pressure.

This has been designed using NP14 Standard Design Tables A.1., A.2. and A.3.

Appendix A Standard Design Tables

Table A.1: Network Analysis Threshold Table for Low & Medium Pressure Systems.

Table A.1. is used to identify the maximum permissible demand that a single/dual supply may take from a parent main of defined diameter without the need for network analysis of the model.

This table should be used when considering:

Low Pressure: Single and Dual Services

Medium Pressure: Single and Dual Services and UIP Mains Connections

Using the diameter of the parent main, compare the maximum permissible demand with the requested Peak Instantaneous Demand (PID). Where the PID does not exceed the indicated value, no additional analysis is required, and design work should progress using standard pressures.

Table A.2: Connection Point Pressures for Low Pressure Systems

Minimum pressure to be supplied for a given level of demand and parent main diameter.

Using the diameter of the parent main, compare the maximum permissible demand with the requested Peak Instantaneous Demand (PID).

Loads falling within the cells highlighted in Yellow will be subject to Post-Acceptance Security of Supply (SoS) checks.

Where the load falls within the Blue line, but is not highlighted in Yellow, no further network analysis is required.

All other loads shall be subjected to network analysis to establish if the required capacity is available. The values in the table will be the minimum supply pressure for these types of request.

Table A.3: Connection Point Design Pressure (loads <2170KW/200scmh) and Minimum Supply Pressure for all MP mains extensions.

The values within this table represent the design pressure that should be used as the start pressure for the design of any connection that:

Is for a load less than 200scmh including services, that is not subject to network analysis.

Provides the minimum design supply pressure from the Wales & West Utilities parent main for a mains system extension.

The system Design Minimum Pressure (DMP) is dependent on the Medium Pressure tier. The grey shaded cells in the above table are not applicable to Medium Pressure networks at present.

Table A.4: Standard Connection Diameter for Multiple Premises Sites (Final connection for GT/UIP requests)

Table A.4 provides guidance on standard connection diameter minimums for mains extensions.

Table A.5: Standard service designs for LP networks

To be used for service connections to LP mains only, using a standard manufacturer’s connection (see Table A.9 & A.10).

Table A.6: Above Ground Standard Service Laterals to Domestic Premises (LP only)

To be used when designing above ground service laterals and laterals to be connected to an above ground riser.

Table A.7: Default service design for all MP systems

Services more than 63m in length should be designed in accordance with the process defined within Appendix B.

Table A.8: Maximum length of pipe to be retained where a large pressure drop (>2mb) is available to be used

This Table should be used to evaluate the design or retention of LP services in conjunction with Table A.2 to avoid the need for Network Analysis to evaluate new demands where:

It is proposed to retain an existing service pipe subject to an increased demand.

It is proposed to install a new service pipe with a pressure drop >2mb (where original design results in a pipe of >=6” NB).

Table A.9: Approved connections for PE pipe to PE mains

Table A9 and A10: Where there is more than one way of installing an approved type of connection, the least cost method will form the basis of any quotation. Only standard manufacturer’s proprietary fittings should be used to provide connection to a Wales & West Utilities system i.e., the use of multiple fittings to provide adequate capacity is prohibited.

Table A.10 Approved connections for PE / Metallic pipe to Metallic mains

Appendix B – Specification for the Design of Pipes

Wherever practicable, the design of a new pipe should be carried out using the relevant “Standard Design Tables” from Appendix A. This will avoid carrying out a bespoke design if the demand and the mains system support the use of a standard design.

This Appendix describes the rules to be used where this is not appropriate. The responsible person should ensure that all pipe design, or design evaluation, is carried out with regard to the requirements of T/PL/NP/16, T/PL/NP/18, and Connections Policy.

Appendix C – Evaluation and Design of Connections to Non-Typical Demands

Where necessary, the relevant demand profile / gas use information should be provided under the Business Rules to allow the provision of a practical design solution.

If this information is incomplete, several simplifying assumptions may be applied resulting in a sub-optimal design solution and additional assessment will be carried out as the type and nature of the installation becomes clear.

Please note that rather than using Table C.1. and C.2. an Additional Load Information Form for Non-Typical Gas Demands is also required.

Appendix D – Specification for Standard Pipe Code Table for New Lay Pipes

When undertaking the design of new system extensions or the review of a 3rd party submissions to be connected to a WWU network, refer to Appendix D. As appropriate, Wales & West Utilities may allow supplementary pipes to be added to the list, i.e., where a UIP proposes to use a non-standard pipe size, which is considered suitable for adoption.

Further Information

Briefing Note 6 - Non-Typical Gas Demands

Briefing Note 7 - Reinforcement Policy

Briefing Note 8 - Sufficiently Complex Job (SCJ) Policy