| # Briefing Note 9: Design Variation |  |
| --- | --- |
| Version 1.0 January 2023 |  |

Table of Contents

1)	Introduction	3

2)	Definition of a Variation	3

3)	WWU Assessment Required	5

4)	Description of Variation Process	5

5)	Verbal Approval	7

6)	SCO	7

Introduction

When there is a need to alter previously approved scope of works, third parties should submit a formal variation for Wales & West Utilities (WWU) approval before the revised works can commence.

As Variations range in complexity, they are categorised into Minor and Major Variations as outlined in IGEM Specification TD/101 and Section 2 of this Briefing Note.

Where a Variation is warranted as per Section 2, the third party should produce a revised design submission that complies to standards cited in WWU Specification NP/14 and submit to WWU Third Party Connections on an FM183 Design Variation Form.

Should the Variation be required due to a Mains Location Error please also see Briefing Note 13 - Mains Location Arrangements For UIP/IGT Connections.

# 2)	Definition of a Variation

WWU recognises the classification of a Minor Variation as per IGEM Specification TD/101 Section 9.3 which lists Minor Variation criteria as:

Increases in pipe depth of 25% to 50% for short distances i.e. to cross under other utilities apparatus or +25% for longer lengths

Decreases in pipe depth of 5% to 10% for short distances i.e. to cross over obstructions, subject to additional pipe protection being installed

Changes in pipe location, provided that there is no change in ownership of land, no easement impacted, and this does not encroach on the minimum property clearance

Short lengths of additional pipe i.e. up to 10M or 10% of designed length, whichever is the least

Change of meter position i.e. up to 2M from original position but still compliant with adopting GT (WWU) standards

Changes in construction methods, provided that the alternative methods have been approved as part of the generic method statements

Minor site layout plans with no impact on designs or meter position compliance

Short reductions in length having no impact on the overall design

WWU recognises the classification of a Major Variation as per IGEM Specification TD/101 Section 9.4 which lists Major Variation criteria as:

Increases/decreases in pipe depth over those stipulated in the note to clause 9.3.3 (i.e. those listed as a Minor Variation)

Changes in pipe location, i.e. footpath to roadway, that encroach on separation distances provided there is no change in ownership of land

Changes in construction methods which are not covered by generic method statements

Major changes to meter position/service entry i.e. from outside the property to inside the property

Decreases in pipework size, changes in materials or any other change that would require a revalidation of the design

Increases and decreases in consumption and modification to consumption pattern

- WWU Assessment Required

Should the Design Variation meet any of the below criteria, the change will need to be assessed by WWU to establish if a new application is required:

The connection is to be moved to a different pressure tier.

The Annual (AQ) and/or Hourly (SHQ) load is changing.

The connection is to be moved to a new main.

If one or more of the above conditions are met, an email must be sent to gtuip@wwutilities.co.uk with an outline of the required change and reason for this. Third Party Connections will review and let you know if further information is required or approve the change.

Description of Variation Process

Third party identify a requirement to alter a proposed scope of works that have been previously approved by WWU

Where the person identifying the Variation is not competent or in a position to do so, they should log the details surrounding the change in line with section A4.1 of IGEM Specification TD/101 and pass to the Designer or a person of authority within their business for appraisal and promotion to WWU.

The Designer within the third party assesses the required changes and identifies whether a Minor or Major Variation is required.

Where the Designer identifies the required changes as a Minor Variation, they should approve the changes in line with section A4.1 of IGEM Specification TD/101 and issue to the Authorising Engineer/Competent Person informing them that works may continue.

  - The Designer should complete a WWU FM183 Design Variation Form and submit to WWU Third Party Connections, with any additional supporting material and a revised design submission, if required

Where the Designer identifies the required changes as a Major Variation they should log the details surrounding the change in line with section A4.1 of IGEM Specification TD/101 and advise any on site Operational colleagues that works must cease until further instruction.

  - The Designer should complete a WWU FM183 Design Variation Form and submit to WWU Third Party Connections, with any additional supporting material and a revised design submission

WWU Third Party Connections will appraise the Variation and, where applicable approve or reject the revised design submission.

  - WWU Third Party Connections will intend to approve revised design approvals within 5 working days.

  - Any decision or production of a revised design drawing due to a Variation should be undertaken by a competent and, where applicable be accredited under GIRS for the required complex.

Verbal Approval

Where applicable, WWU Third Party Connections will approve revised design approvals due to a required Variation within 5 working days, however there are instances where this lead time could have a commercial or financial impact on planned site works. WWU will therefore accept verbal requests for Variation, over the phone in certain instances.

Contact should be made to a WWU Third Party Connections Authorising Engineer from a competent person within the Third Party, who is able to clarify the reasons for Variation and the constraints which warrant only verbal approval.

If verbal approval is granted the name of the WWU Authorising Engineer should be entered onto the FM183 Design Variation Form.

WWU reserves the right to refuse verbal Variation approval or remove the facility entirely without prior notice.

SCO

The approval of a Variation does not preclude the third party from their responsibilities under SCO.